**Clarification of Tender Inquiry for HVAC work in Departure Terminal**

1. Refrigerant pipe: mention sizes.

Ans: This will be as per the vendor’s selection. The selection will be done by software only (as per their make).

1. BoQ Sl No. 10 & 11: Size not mentioned.

Ans: There is a typographical error. The unit will be as “MT²”. Hence size not to mention.

1. BoQ Sl No. 11: not in RMT, its nos.

Ans: The unit is mistake so it is “MT²”.

1. BoQ Sl No. 14 Mention size of dampers.

Ans: It is “MT²”.

1. BoQ Sl No. 16: quantification too much

Ans: This will be as per actual executed quantity. Initial it was considered for whole ducting to be change. However the quantity has been revised in the revised BoQ.

1. Outdoor Unit in BoQ is mentioned as all inverter, however, the specification has mentioned about the partial inverter.

Ans: It is Full inverter. The specification has been modified in the revised specification.

1. Item for “Modification and maintenance of existing duct” need in the BoQ

Ans: The item has been added in the revised BoQ. It is only for the rate as the quantity of ducting to be modified cannot be ascertain.

1. There is lots of miss match between BoQ and technical specification.

Ans: The specification is modified to suit the requirement of BoQ.